## Slide 1
What Does MS4 Mean to You?
A study of sewer and storm drain cross contamination
Presented by Michael Hill, PE and Steve Jepsen
Presented to:

## Slide 2: MS4 and Sanitary Sewer
What will we talk about?
A little about surface water quality regulations
What a sewer agency is doing about them
The goal:
A look at future regulations
Start thinking of how MS4 might affect us…

## Slide 3: What is MS4?
Municipal
Separate
Storm
Sewer
System

## Slide 4: The History of Water Quality
The Roman Empire – 800 BC
The Industrial Revolution – 1800s
The Clean Water Act – 1972
CMOM - 2002
WDR - 2006
MS4 – 2013 (latest version)

## Slide 5: The New MS4
Watershed based
  Water Quality Improvement Plan (WQIP)
  NGO review
Numerical Limits
  TMDL – Total Maximum Daily Limit
  San Diego County estimate 20 year TMDL cost in billions of $
Bacteria TMDLs
Manage new projects to pre-development conditions
Extensive monitoring

## Slide 6: MS4 and Sanitary Sewer
Aren’t we glad we don’t have to deal with this?
Think again…
Bacteria TMDLs are expensive
Storm Water programs do not have direct funding
What is a potential source of bacteria?
How do you prove the sewer is not a source?

## Slide 7: Sewer Exfiltration/MS4 Infiltration
Identify Potential Areas of:
  Sewer Exfiltration
    And –
  Storm Drain Infiltration
Uncommon Situation
Where to Start?
(Sercu et al. 2011, ES&T)

## Slide 8
Each phase narrows search
  Ph I – “Desktop” Portion (GIS, rec dwgs, CCTV)
  Ph II – Field Investigation (CCTV Storm Drains)
  Ph III – Field Testing (dye, soil, sampling)
  Ph IV – Pipe Rehab
Phase I Completed
Phased Approach

## Slide 9: “Desktop” Investigation
Contributing Factors
  Pipe Crossings
  Vertical Separation
  Sewer Pipe Condition
  Storm Drain Mat’l/Size
  Soil Type

## Slide 10: Sewer Collection System
Watershed study area:
  507 sewer pipes
  93,000 ft (18 miles)
Watershed Study Area

## Slide 11: Sewer and Storm Drain System
Watershed Area: 3,200 acres (5 sq.mi )
Investigate:
  Closed Pipe
    And –
  Open Channels
Open Channel Storm Drain
Closed Channel Storm Drain
Sewer Pipe

## Slide 12: Sewer/Storm Drain Crossings
Sewer Crossing Storm Drain
GIS Spatial Queries
Worked w/ City GIS staff
Join storm drain data to sewer data
Join soil data

## Slide 13: GIS Selection Results
107 (21%) sewer pipes selected for further study
Depends on GIS accuracy

## Slide 14: Data Analysis
Exported GIS Data to Excel
Compiled data into categories
Missing Data  Use record drawings

## Slide 15: Scoring Matrix
5 Categories, 12 sub categories
Weighted scoring

## Slide 16: Example Site
Sewer-Storm Drain Crossing
No storm drain invert elevation in GIS
Need IE for scoring

## Slide 17: Example Site (Cont’d)
Review record drawings
1 ft

## Slide 18: Sewer Pipe Deficiency Assessment
Recent CCTV available for all mains
Defects relative to exfiltration

## Slide 19: Phase I Priority Ratings
Based on scoring matrix
Narrow search down
  19 of 507 (4%) sewer pipes above storm drain
  12 of 19 (2%) also cross storm drain
  6 of 12 (1%) also have defect
  2 of 6 (0.3%) also in sandy soil  highest rating
Unaccounted variables/factors

## Slide 20: Phase II and III
Further Narrow Search
Potential sites
Further field work to verify or deny
Rehab pipe is last step

## Slide 21: Questions?
Michael Hill, P.E.
Dudek
mhill@dudek.com
760.479.4124